Parc Place Villas Lift Station Upgrade Scope of Work:

- Remove and replace the existing pumps, panel, floats, valves etc. to upgrade Parc Place Villas lift station to handle the new flow requirements. The lift station concrete vault is to be reused.

- The new design will require a 100 amp service. If the service is not 100 amps, upgrade the wiring, breaker and service as needed.

- Pump truck will be placed on site to keep Parc Place Villas functioning during the replacement work. City Comment: Please be advised that the existing sewer wastewater service to the pump station shall remain in operation during the installation/rehabilitation of the existing pump station in accordance with City of Tampa Wastewater Department Technical Standards Section W-20.

- Clean (pigging) the existing 410 LF of 6” forced main pipe prior to startup of the new system.